## Consultation Questions
BDEW-Beteiligung an der öffentlichen Konsultation zum Strategiepapier zur Überarbeitung des NC RfG und NC DC
The purpose of this consultation is to gather views, feedback and input from all stakeholders on the Policy Paper drafted within the scoping framework of the process. This consultation is addressed to all interested stakeholders. Consulted Policy Paper, planned to be published by September 2022, aims to transparently indicate to stakeholders the areas in which amendments are to be expected, as regards: - Commission Regulation (EU) 2016/631 of 14 April 2016 establishing a network code on requirements for grid connection of generators (NC RfG) - Commission Regulation (EU) 2016/1388 of 17 August 2016 establishing a Network Code on Demand Connection (NC DC)
| Name of the stakeholder | BDEW Bundesverband der Energie- und Wasserwirtschaft e.V.
| Contact person | Benjamin Düvel
| Conacts prsons email adress | benjamin.duevel@bdew.de
| Country | Germany
| Type of stakeholder (generator, consumer, TSO, DSO, academia/research institution, other) | other (whole value chain)
Hinweise im Freigabeverfahren
| Section | BDEW Fassung 10.06. 12 Uhr (nach Freigabe durch Dr. Strobel)
7. Type of stakeolder?
Generator (including association)
Consumer (including association)
Transmission system operator (including association)
Distribution system operator (including association)
Academia/research institution
| Other (please, elaborate) | Yes
| 8. Please, elaborate on your answer above, if necessary: | BDEW represents the whole value chain in electricity and gas (generation/upstream, transmission, distribution, wholesale and retail markets). The following BDEW answers reflect the impact of the Network Codes on the member companies.
9. What is the impact of the NC RfG or NC DC legal requirements on your organisation?
| Direct impact (provisions are applicable to my organisation) | Yes
Possible direct impact (e.g., applicability in the foreseeable future)
Indirect impact (e.g., provisions apply to my contractors)
No relevant impact
I do not want to specify the impact
Other (please, elaborate)
| 10 Please, elaborate on your answer above, if necessary: | Especially the NC RfG legal requirements have a direct impact above all on generators and grid operators.
11. Do you consent to the publication of the stakeholder's name?
| Yes | Yes
No
12. Do you consent to the publication of provided answers?
| Yes | Yes
No
14. Knowing that the exact proposals for amendments will be sought during the public consultation starting in September, please, provide your general comments or views on this Policy Paper, if any:
BDEW strongly supports the review of the NC's. The ACER/CEER Policy Paper presents a solid compilation of the issues which need to be considered and potentially reviewed in the existing grid connection network codes. Some of the issues reflect the work of the European Stakeholder Committee and its expert groups. It is senseful to address a review of the NCs now. In our opinion, the goal should be an applicable rule for all network users, and special requirements should be kept to a minimum. Yet, it must be ensured that existing pump-storage plants are not forced to be decommissoined for economic reasons due to new grid regulations (see below detailed remarks to question no. 17). After release of NC RfG and DCC in 2016, national connection rules have been adapted in accordance with the NCs and have completed them where the NCs asked for concretisation of the non-exhaustive requirements on national level. This concretisation took into account national specificities but it led to a considerable variety of requirements across the EU. When revising the NCs lessons learned from the first NC implementation should be taken into account. The amount of non-exhaustive requirements should be reduced. A stronger harmonisation of requirements will provide a better level playing field for grid users in the EU and drive benefits for the consumers.
15. Is there any area that you consider important but has not been covered by this Policy Paper?
Yes
| No | No
Other
| 16 Please, elaborate on your answer above, if necessary: | The policy paper presents the topics for which a review is needed. Yet, there is some irritation whether there are other processes going on which also work on a review of the Grid Connection Network Codes. It would be helpful if ACER and CEER could explain more precisely how the analysis and recommendations presented in the paper are linked to or based on the work of the European Stakeholder Committee (ESC) on Grid Connection.
17. To what extent do you agree with the policy analysis and recommendations on the requirements for pump storage hydro PGMs:
Strongly agree
Agree
| Neutral | Yes
Disagree
Strongly disagree
| 18 Please, elaborate on your answer above, if necessary: | This topic is a very good example showing that too much rigour on harmonisation does not allow more efficient use of the network and resources for the benefit of consumers. It also shows that specific technology restrictions and capabilities can be well considered in the NCs for maximising the benefit of customers. The main findings of the final report of the expert group "Requirements for pump-storage hydro power generation modules" set up by the GC ESC should be included in the ACER AND CEER POLICY PAPER (draft) (Structural and operational characteristics of pumped storage power plants). The technical requirements of the NC RfG that apply to pump-storage hydro plants must reflect their inherent limitations and possibilities. In the review of the NC RfG as well as in the subsequent amendments to the national rules applicable to Germany - TAR Hochspannung (VDE-AR-N 4120) - , it must be ensured that regulations for pump storage hydro PGMs can be complied with and that the special features of these PGMs as energy storage facilities are taken into account: Pump-storage hydro power plants contribute to the stability of the grid and thus to the stability of the overall system due to their diverse modes of application (energy storage, secondary control power, black start capability / grid reconstruction). The cumulative nature of the capacity and voltage criteria in their current form leads to technical requirements for pump-storage hydro PGMs which are disproportionate compared to their actual impact on the system. This needs to be adjusted in the amendment to avoid disproportionate technical requirements on PGM pumped storage. It must be ensured that existing pump-storage plants are not forced to be decommissioned for economic reasons due to new grid regulations. Especially there must be a protection of vested rights for existing pump-storage plants or, alternatively, investments to meet new grid standards must be reimbursed. Investments in existing pump-storage plants must not be blocked. Therefore a modernisation or extension of existing pumped storage plants must not lead to the loss of the protection of vested rights. The provision of grid services by existing pump-storage plants must not be made more difficult or excluded due to new grid regulations. A final comment is only possible once further concrete information is available in the course of the consultation process. Due consideration must be given to the relevant characteristics and limitations of pumped storage technology.
19. To what extent do you agree with the policy analysis and recommendations on the determination of significance of PGMs:
Strongly agree
| Agree | Yes
Neutral
Disagree
Strongly disagree
Gemeinsame Nutzung von Geodaten zur Umwelt – Bewertung (INSPIRE-Richtlinie) | 20Please, elaborate on your answer above, if necessary: | The significance of small PGMs connected to higher voltage levels has been discussed extensively in the respective expert group in the ESC. The debates showed that the topic is complex. On the one hand, small PGMs (like solar panels) shouldn't be obliged to fulfill the same requirements as larger PGMs. On the other hand, the effect on the grid is the relevant factor which should be decisive for the level of requirements. Resulting from the debates it is clear that there is need for room for national legislators to fine-tune the provisions.
21. To what extent do you agree with the policy analysis and recommendations on the technical requirements for mixed customer sites with generation, demand and storage:
Strongly agree
| Agree | Yes
Neutral
Disagree
Strongly disagree
| 22 Please, elaborate on your answer above, if necessary: | The Policy Paper correctly names the problem and also the difficulties of the possible solutions presented. The intense discussions in the responsible ESC expert group showed that there are very diverse views on this topic. With the decentralisation of electricity production mixed customer sites (MCS) will become an important part of the energy system. On the one hand, new rules have to be easily practicable by the rising number of actors (also households) which both use and produce electricity. On the other hand, the secure grid operation has to remain the leading principle when determining what kind of requirements to MCS are needed. Any proposal for binding rules in a revised network code should be consulted with representatives of grid operators and the grid users affected.
23. To what extent do you agree with the policy analysis and recommendations on the requirements for type A PGMs:
Strongly agree
Agree
| Neutral | Yes
Disagree
Strongly disagree
| 24 Please, elaborate on your answer above, if necessary: | The main findings from the final report of the expert group "Baseline for Type A power-generating modules" (EG BftA) under the Grid Connection ESC should be included in the ACER and CEER Policy Paper [interner Hinweis an BDEW-Gremien: EG BftA Report hängt der Gremien-E-Mail vom 03.06.22 an]. It will only be possible to comment on the threshold values once further concrete information is available in the course of the consultation procedure. It is comprehensible that manufacturers pledge for a harmonisation of the threshold between type A and type B Power generating modules (PGMs) across Europe. Yet, there mustn't be cutbacks to requirements which are necessary to ensure system safety. It has to be thoroughly analysed which requirements for type B PGMs are not necessary to be fulfilled by PGMs which are close to the type A threshold. In these areas, a pan-European harmonisation is possible. For existing PGMs, the continued applicability of existing rules must be ensured.
25. To what extent do you agree with the policy analysis and recommendations on the significant modernisation:
Strongly agree
| Agree | Yes
Neutral
Disagree
Strongly disagree
| 26 Please, elaborate on your answer above, if necessary: | The criteria according to which an amendment to a PGM must be considered a substantial revision are to be specified more clearly in order to avoid significantly different requirements in the Member States. The exact implementation of these criteria will have to be the task of the national concretisation, along with the concretisation of the general requirements. A final comment on this issue will only be possible once further concrete information is available in the course of the consultation process.
27. To what extent do you agree with the policy analysis and recommendations on the technical requirements for storage:
Strongly agree
| Agree | Yes
Neutral
Disagree
Strongly disagree
| 28 Please, elaborate on your answer above, if necessary: | Including technical requirements for storage into the NC RfG and DCC would ensure harmonisation of rules across Europe as well as equal treatment of with power plants and other network users. In this respect, the relevant characteristics and limitations of storage technologies shall be duly taken into account in order to provide sufficient flexibility for connecting new upcoming technologies.
29. To what extent do you agree with the policy analysis and recommendations on the electromobility:
Strongly agree
Agree
| Neutral | Yes
Disagree
Strongly disagree
| 30 Please, elaborate on your answer above, if necessary: | Any policy recommendation must a) secure the integration of e-mobility into the grid infrastructure, b) reach standardisation without imposing unreasonable costs onto the users and c) support the opportunity to use the potentials of electromobility to facilitate the energy transition. Furthermore, it has to be considered that: a) There is a significant difference between private and public chargers; technical requirements regarding the latter ones are already regulated by the Alternative Fuel Infrastructure Directive (remark: The AFID will be transformed into a regulation soon); b) The focus of the DSOs is on the grid connection point and not the chargers behind it. c) The described options only consider reactive actions between grid and charger. There is also a need for interaction and communication between the market participants.
31. To what extent do you agree with the policy analysis and recommendations on the simulation models and compliance monitoring:
Strongly agree
Agree
| Neutral | Yes
Disagree
Strongly disagree
| 32 Please, elaborate on your answer above, if necessary: | A validated simulation model is useful. However, several points need to be clarified: a.) For which systems / components are simulation models required? b.) Simulation scope/scope c.) Clear specifications on the scope and content of the simulation in order to avoid multiple loops during simulation creation d.) Cost bearing / cost sharing in case of iteration of the simulation models in the course of component development or due to further simulation requirements on the part of the grid operator e.) Duration of the final simulation coordination between power plant operator / plant manufacturer and grid operator in the case of replacement of plants or new plants f.) Protection of the status quo for simulations already created or cost bearing by the grid operator A final comment is only possible once further concrete information is available in the course of the consultation process. Any amendment should be an outcome of a comprehensive stakeholder consultation process and also reflect the ongoing developments at international standardisation organisations (IEC et. al.) on simulation model standardisation and model validation.
33. To what extent do you agree with the policy analysis and recommendations on the advanced capabilities for grids with high penetration of DER:
Strongly agree
Agree
| Neutral | Yes
Disagree
Strongly disagree
| 34 Please, elaborate on your answer above, if necessary: | BDEW supports any initiative for making distribution systems smarter and utilising the assets more efficiently. Distribution networks need to develop towards distribution systems. This should also trigger updates on the regulatory regime and the introduction of specific ancillary services for distribution systems (e. g. but not limited to reactive power provision for voltage control services). Such developments must by no means hinder further investments in distribution systems for making them more effective by building new assets to integrate an even larger amount of distributed renewable generators. Yet, the ACER / CEER analysis is limited to the grid operator's perspective. Also the consequences to market actors and final customers have to be taken into account.
35. To what extent do you agree with the policy analysis and recommendations on the requirements for weather hazards resilience of generators:
Strongly agree
Agree
| Neutral | Yes
Disagree
Strongly disagree
| 36 Please, elaborate on your answer above, if necessary: | The overall system must be set up in such a way that resilience to weather hazards can be improved and generator failures can be compensated for. However, this cannot be achieved by continuously increasing the requirements for generators of existing plants with the revision of regulations. As expected, this will only be possible within narrow limits. Protection of existing plants must be taken into account. A final comment is only possible once further concrete information is available in the course of the consultation process.
37. To what extent do you agree with the policy analysis and recommendations on the technical requirements for active customers/energy communities:
Strongly agree
Agree
Neutral
| Disagree | Yes
Strongly disagree
| 38 Please, elaborate on your answer above, if necessary: | Any review of the NC RfG and NC DC has to be in line with the upcoming NC on Distributed Flexibility and mustn't prejudice the provisions to be laid down in the latter NC.
39. To what extent do you agree with the policy analysis and recommendations on the requirements for units providing demand response services:
Strongly agree
Agree
| Neutral | Yes
Disagree
Strongly disagree
| 40 Please, elaborate on your answer above, if necessary: | Any review of the NC RfG and NC DC has to be in line with the upcoming NC on Distributed Flexibility and mustn't prejudice the provisions to be laid down in the latter NC.